## A5 form
ALPHA TECHNOLOGIES LTD TEST RESULTS |  |  |  | Drawing No: | 0100048-A5
Product | POWER MODULE, CXRF-HP 380-5kW |  |  | Tested By: | $!Tested_By
Part No: | $!Part_No |  |  | Test Station: | $!station_ID
Serial No: | $!Serial_No
Date: | $!Test_Date
Test No. | Test Description | Result | UoM | MIN | MAX | PASS
6. | FINAL TEST PROCEDURE
6.1. | Burn In Procedure | $!6.1. | P/F/N
6.2. | HIPOT Test | $!6.2. | P/F/N
6.3. | Ground Continuity Test | $!6.3. | P/F/N
6.4. | Startup and LEDs Test
6.4.3. | All 3 LEDs illustrate correct color | $!6.4.3. | P/F/N
6.4.4. | Green AC and DC - ON, Red FAIL LEDs - OFF | $!6.4.4. | P/F/N
6.4.5. | Output Voltage | $!6.4.5. | V | 53.4 | 54.6
6.5. | Line Regulation
6.5.5. | Output voltage change | $!6.5.5. | V | -0.4 | 0.4
6.6. | Diag Tool
6.6.3. | Device name, Serial Number and S/W Rev. Verification | $!6.6.3. | P/F/N
6.6.4. | OVP setting, V=63V | $!6.6.4. | P/F/N
6.6.5. | Current limit setting, 100% | $!6.6.5. | P/F/N
6.6.6. | Power limit setting, 100% | $!6.6.6. | P/F/N
6.7. | Float Voltage Verification
6.7.2. | Float Voltage Maximum | $!6.7.2. | V | 57.4 | 58.6
6.7.4. | Float Voltage Minimum | $!6.7.4. | V | 47.4 | 48.6
6.7.5. | Float Voltage Setup, V=54V | $!6.7.5. | V | 53.4 | 54.6
6.8. | Load Regulation, Output Voltage and Current Accuracy
6.8.3. | Output voltage change | $!6.8.3. | V | -1 | -0.15
6.8.4. | Output current error | $!6.8.4. | A | -2.5 | 2.5
6.8.5. | Output voltage error | $!6.8.5. | V | -0.6 | 0.6
6.9. | Power Limit, Current Limit, Short Circuit
6.9.1. | Output Voltage | $!6.9.1. | V | 51.5 | 52.5
6.9.2. | Output Current | $!6.9.2. | A | 42.4 | 48
6.9.3. | Output power | $!6.9.3. | W | 2225 | 2475
6.9.6. | Output current | $!6.9.6. | A | 48 | 52
6.9.10. | Short circuit current | $!6.9.10. | A | 28 | 46
6.10. | Safe Mode Voltage, V=51.4V | $!6.10. | P/F/N
$!Comments
Note on F37: =F35*F36